## Slide 1: Gas Turbine Thermodynamics Features
at least the system contains the combination of a single turbine, a combustion chamber and a (bladed) compressor;
turbine blades are continuously in contact with a gas of high temperature - natural limit of cycle parameters (blades loaded by centrifugal force, creep limits);
an ICE without a high temperature heat exchanger for heat supply - instead of it a combustion chamber; heat rejection via exchange of burnt gas/fresh air, which is substituted in T-s diagram by equivalent (isobaric or almost isobaric) change with the same energy transfer (in reality change of enthalpy)
compression before combustion needed not only for temperature increase but also it provides flow through turbine blades - circulating power turbine-compressor loaded by losses;
low-pressure regenerating heat exchanger enhances efficiency if pressure ratio is too low;
maximum pressure influences turbine price - multi stages machines small and efficient but expensive

## Slide 2: Simplest lay-out of a gas turbine
Single-shaft turbine - in reality multi-stage one (and the same for compressor) - required for high efficiency. Quadratic dependence between speed and pressure ratio - suitable for constant speed only (e.g., alternator load).

## Slide 3: Gas turbine with heat regeneration
Single-shaft turbine with exhaust heat regeneration suitable for single- or two-stage with low pressure ratio and constant speed loads.

## Slide 4: T-s diagrams of an ideal gas turbine with different pressure ratio and w/o or w/t heat regeneration from exhaust to compressed air
hT
hK
T-s Diagram of Ideal Gas Turbine
pressure ratio =10; TT1=1 200 K; C =T=1
Brake efficiency 46.2% ... b.s.f.c. 182 g/kW/h
air excess 4.3; total pressure loss HP 0 kPa, LP 0 kPa
T-s Diagram of Ideal Gas Turbine with Regeneration
pressure ratio =5; TT1=1 200 K; C =T=100%
Brake efficiency 60.1% ... b.s.f.c. 140 g/kW/h
air excess 6.5; total pressure loss HP 0 kPa, LP 0 kPa
regenerator efficiency 100% (see the next slide)

## Slide 5: Isentropic efficiencies – definition and T-s. Examples of real cycles with regeneration
T-s Diagram of Real Gas Turbine with Regeneration
pressure ratio =5; TT1=1 200 K; C =T=85%
Brake efficiency 18.7% ... b.s.f.c. 453 g/kW/h
air excess 7.9; total pressure loss HP 35 kPa, LP 42 kPa
regenerator efficiency 80%
T-s Diagram of Real Gas Turbine with Regeneration
pressure ratio =7; TT1=1 200 K; C =T=85%
Brake efficiency 30.9% ... b.s.f.c. 273 g/kW/h
air excess 6.3; total pressure loss HP 4 kPa, LP 19 kPa
regenerator efficiency 80%

## Slide 6: Gas turbine – real cycles, influence of heat regeneration; pi K = 10
T-s Diagram of Real Gas Turbine without Regeneration
pressure ratio =10; TT1=1 200 K; K =T=85%
Brake efficiency 24.1% ... b.s.f.c. 350 g/kW/h
air excess 4.7; total pressure loss HP 1.5 kPa, LP 14 kPa
T-s Diagram of Real Gas Turbine
pressure ratio =10; TT1=1 200 K; K =T=85%
Brake efficiency 28.2% ... b.s.f.c. 299 g/kW/h
air excess 5.8; total pressure loss HP 2 kPa, LP 19 kPa
regenerator efficiency 80%

## Slide 7: Gas turbine efficiency for different lay-outs
big dependence on thermodynamic isentropic efficiencies of compression and expansion;
limited by maximum temperature, which acts continuously at turbine blades;
regeneration of exhaust enthalpy to pre-heating of air possible at low pressure ratio; it causes pressure losses and depends on heater efficiency.

## Slide 8: Gas turbine b.s.f.c. for different lay-outs and efficiencies at 1 200 K
Chart: 
| 2 | 3 | 4 | 5 | 6 | 8 | 10 | 15 | 20
eC=.75/eT=.7/eHE=.8 | 604.976 | 459.1222 | 463.218 | 502.0751 | 563.4376 | 770.8618 | 1197.5435 | 1197.5435 | 1197.5435
eC=.8/eT=.75/eHE=.8 | 456.0703 | 341.5909 | 330.5458 | 339.2017 | 356.3545 | 407.3211 | 477.26 | 811.7059 | 1834.4946
eC=.85/eT=.85/eHE=.8 | 335.7417 | 253.1989 | 239.3473 | 238.1338 | 241.5966 | 254.7766 | 271.9854 | 325.6029 | 345.4622
eC=.85/eT=.85/no HE | 961.2914 | 548.5116 | 442.9244 | 394.1462 | 366.6494 | 338.166 | 326.3259 | 325.0204 | 345.4571
eC=.8/eT=.8/eHE=.8 | 399.2154 | 300.4615 | 287.9229 | 291.4878 | 301.4411 | 331.7705 | 371.2493 | 523.0136 | 696.7618
eC=.8/eT=.8/eHE=.6 | 595.7674 | 393.9757 | 353.6729 | 343.0105 | 343.7328 | 361.4999 | 391.8982 | 522.858 | 774.9213

## Slide 9: Gas turbine b.s.f.c. for different lay-outs and efficiencies at 1 500 K

## Slide 10: Combustion turbine – proposal for constant cross-section of gas tract